Virtual AC Changeout Inspection on Demand

AC Changeout

- Onsite have permit and AHRI available.

- Call Alphanette @386-986-7982 or Chris @ 386-286-2054.

- Ask if she/he can do a virtual inspection. Allow 15 minutes to prep. Call back via FaceTime or Google Meet

Exterior

- Show street view of the structure where 911 address is visible.

- Show unit level and anchored to pad with locking caps and UV protected insulation for refrigerant line.

- Show ac unit label with model # and max overcurrent visible, whip attached to structure, disconnect accessible, and condensate draining 12” from foundation.

Interior at Electric Panel

- Show AH (heat) breaker size and AC (condenser) breaker size.

Ensure breakers are compatible with panel.

- If unit is in the attic, a notice is required at the panel indicating location.

Interior at air handler

- Show AH connected.  Show air handler label with model # and heat strips and maximum overcurrent protection.

- Show duct connections to unit, float switch or secondary drain, pan, if applicable, insulation on condensate lines, if applicable, and sealant at penetrations in ceiling.

INSPECTION COMPLETE